# Text boxes

QLC/TB-RFI

(110v)

X10787

PHASE ANGLE ELECTRONIC HEAT SWITCH

WITH RFI SUPPRESSION (110v)

INTRODUCTION

These switched phase-angle power regulators are robust and compact units are ideal for controlling single/phase mains driven loads.  These QLC units are for 110VAC supply, with a three position (and off) control switch with wiring connections to the plug-in five way terminal.  The large triac enables the unit to handle high inrush current with ample safety margins on industrial installations.  These units incorporate their own RFI filter which will aid product compliance when correctly installed.

APPLICATIONS

Suitable for quartz lamps, conventional resistive heating elements in single phase, series or parallel configurations to the specified voltage, current and temperature limits and inductive loads, for example, transformers and motors.

## FEATURES

- Integrated RFI network.

- Plug in power connector block.

- Single-hole fixing.

- Rugged and compact.

- Designed to maximise thermal dissipation.

RoHS Compliant

| POSITION | ac O/P LOADED VOLTS (rms typical) |
| --- | --- |
| 0 | ZERO |
| 1 | 80 |
| 2 | 90 |
| 3 | SUPPLY |

INSTALLATION

DIMENSIONS, WIRING CONNECTIONS & OUTPUTS

INSTALLATION

SPECIFICATIONS AND DIMENSIONS

Unit limiting rms on state current		15A		Maximum forward voltage drop at 15A		1.5V

Triac limiting rms on state current		25A		Peak one cycle surge @ (10ms)		320A

Mains supply, tolerance, within 10%		110V AC		I2t limiting value for fusing			112A2s                Isolation voltage		2.5kV rms	Mains frequency				50/60Hz

Max recommended operational temperature	65ºC		Max. recommended storage temperature	65ºC

Dimensions approximate

Shaft diameter		6.3 mm (1/4”)	Bush length				5 mm

Shaft projection from bush	30 mm	Fixing hole diameter				10mm

FUSING

It is recommended to use semiconductor (fast-acting) type fuses or circuit breakers (semiconductor - MCB) for protection. On initial use some loads may need an increased factor of safety for unit and/or device protection (see SRA data sheet for further information).

CE MARKING

This product family carries a CE mark and incorporates a built-in filter. For information see recommendation section and contact our sales desk (see Declaration of Conformity).

RECOMMENDATIONS

Other documents available on request, which may be appropriate for your application: -

CODE	IDENTITY	DESCRIPTION

X10229	RFI	Single Phase Filtering recommendations - addressing EMC Directive

X10213	ITA	Interaction, uses for phase angle and for burst fire control.

X10255	SRA	Safety requirements - addressing the Low Voltage Directive (LVD) including:

thermal data/cooling, live parts warning, earth requirements and fusing

recommendations.

X10378                              ILR                      Inductive loads remedy sheet for use with Phase angle controllers

P01.1	COS	UAL conditions of sale.

NOTE:  It is recommended that installation and maintenance of this equipment should be done with reference to the current edition of the I.E.T. (formally I.E.E.) regulations (BS7671) by suitably qualified/trained personnel. The regulations contain important requirements regarding installation and safety of electrical equipment. Specific installers should refer to local and national regulations.

ORDER CODE:  	State part number:	QLC-RFI-TB (110v) (Other voltage inputs and outputs available)

Optional extras include:	knob, dial, heatsink compound.

UNITED AUTOMATION LIMITED

Southport Business Park		 Tel:  0044 (0) 1704 – 516500

Wight Moss Way			 Fax: 0044 (0) 1704 – 516501

Southport, PR8 4HQ		 enquiries@united-automation.com

ENGLAND			 www.united-automation.com

Page No. 2 of 2   		       Issue 2 		Date  19/02/19